## Pipe_Flow_Calc
ENGINEERING DESIGN CALCULATION
Pipe and Fittings Pressure Drop Calculation (refer Crane Flow of Fluids)
| Client: | Holly Refining |  |  | Project: |  | E08-297HOL
| Task: | check accuracy of the orifice calc |  |  | By: |  | Trevor Kanode
P1
| H1 |  |  | P1p
H1p
T, r, m
L, d, v, Kp, Kf
|  |  | Q, v, Re, f | [7 empty] | P2
H2
H2p
|  |  | Reference Elevation |  | P2p
| Upstream Conditions: |  |  |  | Downstream Conditions:
| At Fluid Surface: |  |  |  | At Fluid Surface:
| Pressure | P1 | 301 | psi(g) | Pressure |  | P2 |  | #VALUE! |  | psi(g)
| Elevation | H1 | 0 | ft | Elevation |  | H2 |  | 0 |  | ft
| At Pipe Inlet: |  |  |  | At Pipe Inlet:
| Elevation | H1p | 0 | ft | Elevation |  | H2p |  | 0 |  | ft
| Pressure | P1p | 301 | psi(g) | Pressure |  | P2p |  | #VALUE! |  | psi(g)
| Pipe Size: |  |  |  | Fluid Details:
|  | Reference Pipe Size |  |  |  |  | Fluid Type |  | Sour NGL
|  | Size (in) | 2 |  |  |  | T |  | 100 |  | oF
|  | Sched | 80 |  |  |  | r |  | 31.72 |  | lb/ft3
|  | Type | 6 |  |  |  | m |  | 0.13 |  | cP
|  |  | Steel Pipe-clean |  | Fluid Flow:
|  | v | 0.00016404 | ft |  |  | Q |  | 83.6 |  | gal/min
|  | d | 1.9378 | in |  |  | q |  | 21269.5802 |  | lb/hr
| Pipe K Factor: | Kp | #VALUE! |  |  |  | q |  | 11.1757 |  | CFM
| Fittings K Factor: | Kf | #VALUE! |  |  |  | q |  | #VALUE! |  | MMSCFD
| Valves K Factor: | Kv | #VALUE! |  |  |  | v |  | 9.0945 |  | ft/sec
|  | Ktot | #VALUE! |  |  |  | Re |  | 532850.244
|  | Le(ref) | #VALUE! | ft |  |  | f |  | #VALUE!
[7 empty] | fT (fully turbulent flow) |  | #VALUE!
| Solver Options: | [5 empty] | dPfrict |  | #VALUE! |  | psi
[7 empty] | dPelev |  | 0 |  | psi
[7 empty] | dPtotal |  | #VALUE! |  | psi
[7 empty] | dPf/P1 |  | #VALUE!
[7 empty] | dPf/100ft |  | #VALUE! |  | psi/100ft
| Pipe Details: |  | Size (in) |  | 2 |  | 1 |  | 3 |  | 4
|  |  | Sched |  | 80 |  | 160 |  | 40 |  | 40
|  |  | Type |  | 6 |  | 6 |  | 6 |  | 6
[5 empty] | Steel Pipe-clean |  | Steel Pipe-clean |  | Steel Pipe-clean |  | Steel Pipe-clean
|  |  | v | ft | 0.00016404 |  | 0.00016404 |  | 0.00016404 |  | 0.00016404
|  |  | NB | mm | 50 |  | 25 |  | 80 |  | 100
|  |  | OD | in | 2.374 |  | 1.315 |  | 3.5 |  | 4.5
|  |  | WT | in | 0.21811 |  | 0.25 |  | 0.21614 |  | 0.23701
|  |  | d | in | 1.9378 |  | 0.81496 |  | 3.0677 |  | 4.026
|  |  | L | ft | 0
|  |  | v | ft/sec | 9.0945 |  | 51.4189 |  | 3.6288 |  | 2.1069
|  |  | Re |  | 532850.244 |  | 1266999.469 |  | 336587.3846 |  | 256472.6091
|  |  | f |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE!
|  |  | fT |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE!
|  |  | Kp |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE!
|  |  | Le | ft | #VALUE! | #DIV/0! | #VALUE! | #DIV/0! | #VALUE! | #DIV/0! | #VALUE!
|  |  | dPfrict | psi | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE!
|  |  | dP/100ft | psi | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE!
|  |  | Kp(ref) |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE!
|  |  | Le(ref) | ft | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE!
| Fittings Details: |  |  | Size | 2 | fT | 1 | fT | 3 | fT | 4 | fT
| Note: Enter reducers under the smaller size |  |  | K/fT or K | 1.9378 | #VALUE! | 0.81496 | #VALUE! | 3.0677 | #VALUE! | 4.026 | #VALUE!
| Elbow B/W | 90 | 1 | 20 |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE!
|  |  | 1.5 | 14 |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE!
|  |  | 2 | 12 |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE!
|  |  | 3 | 12 |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE!
|  |  | 4 | 14 |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE!
|  |  | 6 | 17 |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE!
|  |  | 8 | 24 |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE!
|  |  | 10 | 30 |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE!
|  |  | 12 | 34 |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE!
|  |  | 14 | 38 |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE!
|  |  | 16 | 42 |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE!
|  |  | 20 | 50 |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE!
|  | 45 | SR (r/d=1) | 15 |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE!
|  |  | LR (r/d=1.5) | 10 |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE!
|  | 180 | SR (r/d=1) | 30 |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE!
|  |  | LR (r/d=1.5) | 22 |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE!
| Other | 180 | 4 | 24.1416 |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE!
| Mitre Bend | Angle | 0 | 2 |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE!
|  |  | 15 | 4 |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE!
|  |  | 30 | 8 |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE!
|  |  | 45 | 15 |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE!
|  |  | 60 | 25 |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE!
|  |  | 75 | 40 |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE!
|  |  | 90 | 60 |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE!
| Tee B/W | Thru Run |  | 7.5 |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE!
|  | Thru Branch |  | 35 |  |  |  | #VALUE! |  | #VALUE! |  | #VALUE!
| Pipe Entry | Projecting |  | 0.78 |  |  |  | 0 |  | 0 |  | 0
|  | Flush | Sharp | 0.5 |  |  |  | 0 |  | 0 |  | 0
|  |  | Rounded 0.1 | 0.09 |  |  |  | 0 |  | 0 |  | 0
| Pipe Exit | Projecting |  | 1 |  |  |  | 0 |  | 0 |  | 0
|  | Flush | Sharp | 1 |  |  |  | 0 |  | 0 |  | 0
|  |  | Rounded 0.1 | 1 |  |  |  | 0 |  | 0 |  | 0
| Contraction ANSI | d1/d2= | 0.4 | 36 |  |  |  | 0 |  | 0 |  | 0
| Included angle < 45o |  | 0.5 | 30 |  |  |  | 0 |  | 0 |  | 0
|  |  | 0.6 | 23 |  |  |  | 0 |  | 0 |  | 0
|  |  | 0.75 | 18 |  |  |  | 0 |  | 0 |  | 0
|  |  | 0.8 | 10 |  |  |  | 0 |  | 0 |  | 0
|  | other | 0.7 | 20 |  |  |  | 0 |  | 0 |  | 0
| Enlargement ANSI | d1/d2= | 0.4 | 36 |  |  |  | 0 |  | 0 |  | 0
| Included angle < 45o |  | 0.5 | 30 |  |  |  | 0 |  | 0 |  | 0
|  |  | 0.6 | 23 |  |  |  | 0 |  | 0 |  | 0
|  |  | 0.75 | 18 |  |  |  | 0 |  | 0 |  | 0
|  |  | 0.8 | 10 |  |  |  | 0 |  | 0 |  | 0
|  | other | 0.62 | 21 |  |  |  | 0 |  | 0 |  | 0
| Contraction Sudden | d1/d2= | 0.5 | 180 |  |  |  | 0 |  | 0 |  | 0
| Enlargement Sudden | d1/d2= | 0.6 | N/A |  | 0 |  | 0 |  | 0 |  | 0
Included angle > 45o
|  |  |  | Kf | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE!
| Note: Enter reducers under the smaller size |  |  | Kf(ref) | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE!
| Valve Details: | Type |  | Size | 2 | fT | 1 | fT | 3 | fT | 4 | fT
|  |  |  | K/fT | 1.9378 | #VALUE! | 0.81496 | #VALUE! | 3.0677 | #VALUE! | 4.026 | #VALUE!
| Gate | FB |  | 8 |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE!
|  | RB | d1/d2=b | 0.666
|  |  | a | 15 |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE!
| Plug | Parallel | d1/d2=1 | 18 |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE!
|  |  | d1/d2=b | 0.77
|  |  | a | 16 |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE!
| Ball | FB |  | 3 |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE!
|  | RB | d1/d2=b | 0.77
|  |  | a | 23 |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE!
| Butterfly |  |  | 45 |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE!
| Check | Swing | Angle Seat | 100 |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE!
|  |  | Vert Seat | 50 |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE!
|  | Lift Check | Hor Seat | 600 |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE!
|  | (d1/d2=1) | Angle Seat | 55 |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE!
|  | Wafer |  | Varies |  | #VALUE! |  | 0 |  | #VALUE! |  | #VALUE!
|  | Axial |  |  |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE!
| Foot Valve | Vertical Disc |  | 420 |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE!
|  | Hinged Disc |  | 75 |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE!
| Globe (d1=orifice) | Inline | d1/d2=1 | 340 |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE!
|  | Angled | d1/d2=1 45o | 55 |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE!
|  |  | d1/d2=1 90o | 150 |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE!
|  | Inline Red. | d1/d2=b | 0.9 |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE!
| Orifice Plate (Flange Tap Only) |  | Beta Ratio | 0.693 |  | 0 |  | 0 |  | 0 |  | 0
| (Valid for 0.3<b<0.7) |  | Flow Coefficient C | 0.6868
Other
| Stockham Wafer Check 2 in |  | Cv= | 54.3 |  | 0 |  | 0 |  | 0 |  | 0
| Stockham Wafer Check 3 in |  | USGPM | 139.3 |  | 0 |  | 0 |  | 0 |  | 0
| Stockham Wafer Check 4 in |  |  | 271.3 |  | 0 |  | 0 |  | 0 |  | 0
| Stockham Wafer Check 6 in |  |  | 725 |  | 0 |  | 0 |  | 0 |  | 0
| Stockham Wafer Check 8 in |  |  | 1509 |  | 0 |  | 0 |  | 0 |  | 0
| Stockham Wafer Check 10 in |  |  | 2640 |  | 0 |  | 0 |  | 0 |  | 0
| Stockham Wafer Check 12 in |  |  | 4075 |  | 0 |  | 0 |  | 0 |  | 0
| Kitz Ball RB 2 in |  |  | 160 |  | 0 |  | 0 |  | 0 |  | 0
| Kitz Ball RB 3 in |  |  | 440 |  | 0 |  | 0 |  | 0 |  | 0
| Kitz Ball RB 4 in |  |  | 780 |  | 0 |  | 0 |  | 0 |  | 0
| Kitz Ball RB 6 in |  |  | 1500 |  | 0 |  | 0 |  | 0 |  | 0
| Kitz Ball RB 8 in |  |  | 1700 |  | 0 |  | 0 |  | 0 |  | 0
| Kitz Ball RB 10 in |  |  | 3100 |  | 0 |  | 0 |  | 0 |  | 0
| Kitz Ball RB 12 in |  |  | 5800 |  | 0 |  | 0 |  | 0 |  | 0
| Richards Ball RB (Series 11) 2 in |  |  | 115 |  | 0 |  | 0 |  | 0 |  | 0
| Richards Ball RB (Series 11) 3 in |  |  | 320 |  | 0 |  | 0 |  | 0 |  | 0
| Richards Ball RB (Series 11) 4 in |  |  | 600 |  | 0 |  | 0 |  | 0 |  | 0
| Richards Ball RB (Series 11) 6 in |  |  | 1000 |  | 0 |  | 0 |  | 0 |  | 0
| Richards Ball RB (Series 11) 8 in |  |  | 2000 |  | 0 |  | 0 |  | 0 |  | 0
| Starline Ball RB 2 in |  |  | 125 |  | 0 |  | 0 |  | 0 |  | 0
| Starline Ball RB 3 in |  |  | 319 |  | 0 |  | 0 |  | 0 |  | 0
| Starline Ball RB 4 in |  |  | 580 |  | 0 |  | 0 |  | 0 |  | 0
[6 empty] | 0 |  | 0 |  | 0 |  | 0
[6 empty] | 0 |  | 0 |  | 0 |  | 0
| 1" EZ with 3/4" Port |  |  | 8.84 |  | 0 |  | 0 |  | 0 |  | 0
| 2" EZ with 2" port =% |  |  | 53.8 |  | 0 |  | 0 |  | 0 |  | 0
| 1-1/2" Fisher ED 75% of max Cv |  |  | 26.9 |  | 0 |  | 0 |  | 0 |  | 0
[6 empty] | 0 |  | 0 |  | 0 |  | 0
[6 empty] | 0 |  | 0 |  | 0 |  | 0
Other
|  |  | K= | 5.42 |  | 0 |  | 0 |  | 0 |  | 0
[6 empty] | 0 |  | 0 |  | 0 |  | 0
[6 empty] | 0 |  | 0 |  | 0 |  | 0
[6 empty] | 0 |  | 0 |  | 0 |  | 0
[6 empty] | 0 |  | 0 |  | 0 |  | 0
[6 empty] | 0 |  | 0 |  | 0 |  | 0
[6 empty] | 0 |  | 0 |  | 0 |  | 0
[6 empty] | 0 |  | 0 |  | 0 |  | 0
[6 empty] | 0 |  | 0 |  | 0 |  | 0
[6 empty] | 0 |  | 0 |  | 0 |  | 0
[6 empty] | 0 |  | 0 |  | 0 |  | 0
[6 empty] | 0 |  | 0 |  | 0 |  | 0
[6 empty] | 0 |  | 0 |  | 0 |  | 0
[6 empty] | 0 |  | 0 |  | 0 |  | 0
[6 empty] | 0 |  | 0 |  | 0 |  | 0
|  |  |  | Kv | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE!
|  |  |  | Kv(ref) | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE!
^^^^^ Given P2 (psig) find Q
^^^^^ Given v (ft/s) find Q, P2
^^^^^ Given P2 (psig) find H2
Enter the required values and solve as indicated
CLEAR ALL DATA FROM WORKSHEET
Instructions: Calculates Liquid or Gas flow through a pipe system comprising pipe, fittings and valves of up to four different sizes.
For gas flows dPf/P1 should not exceed 10%.
Any one of the pipe sizes may be used as the Reference Pipe Size though the smallest size should be considered.
The calculation finds P2 for a given H2 and Q by default but
it can also solve for a given P2 or velocity (in the ref pipe size) by entering the required value and selecting the Solver button.
Select the size, schedule and type (1 to 17) of pipe and provide the length of each.
Select the type and number of fittings of each size in the line.
Select the type and number of valves of each size in the line.
Where valve manufacturers data is available as Cv or K values these may be entered.
The library provides a storage area for valve Cv and K values.

## Library
Engineering Design Calculation - Dennis Kirk
| Component | USGPM | Cv= | Component | UKGPM | Cv= | Component | K=
| Stockham Wafer Check 2 in |  | 54.3
| Stockham Wafer Check 3 in |  | 139.3
| Stockham Wafer Check 4 in |  | 271.3
| Stockham Wafer Check 6 in |  | 725
| Stockham Wafer Check 8 in |  | 1509
| Stockham Wafer Check 10 in |  | 2640
| Stockham Wafer Check 12 in |  | 4075
| Stockham Wafer Check 14 in |  | 5303
| Stockham Wafer Check 16 in |  | 7340
| Stockham Wafer Check 18 in |  | 9940
| Stockham Wafer Check 20 in |  | 12960
| Stockham Wafer Check 24 in |  | 20500
| Stockham Wafer Check 30 in |  | 37200
| Stockham Wafer Check 36 in |  | 59000
| Kitz Ball RB 2 in |  | 160
| Kitz Ball RB 3 in |  | 440
| Kitz Ball RB 4 in |  | 780
| Kitz Ball RB 6 in |  | 1500
| Kitz Ball RB 8 in |  | 1700
| Kitz Ball RB 10 in |  | 3100
| Kitz Ball RB 12 in |  | 5800
| Richards Ball RB (Series 11) 2 in |  | 115
| Richards Ball RB (Series 11) 3 in |  | 320
| Richards Ball RB (Series 11) 4 in |  | 600
| Richards Ball RB (Series 11) 6 in |  | 1000
| Richards Ball RB (Series 11) 8 in |  | 2000
| Starline Ball RB 2 in |  | 125
| Starline Ball RB 3 in |  | 319
| Starline Ball RB 4 in |  | 580
| Kitz Ball FB 2 in |  | 450
| Kitz Ball FB 3 in |  | 1300
| Kitz Ball FB 4 in |  | 2200
| Kitz Ball FB 6 in |  | 5000
| Kitz Ball FB 8 in |  | 10000
| Kitz Ball FB 10 in |  | 17000
| Kitz Ball FB 12 in |  | 25000
| TK Ball FB 1/2 in | Class 150 | 16
| TK Ball FB 1/2 in | Class 300 | 14
| TK Ball FB 1/2 in | Class 600 | 12
| TK Ball FB 1/2 in | Class 900 | 11
| TK Ball FB 1/2 in | Class 1500 | 11
| TK Ball FB 1/2 in | Class 2500 | 10
| TK Ball FB 3/4 in | Class 150 | 44
| TK Ball FB 3/4 in | Class 300 | 38
| TK Ball FB 3/4 in | Class 600 | 34
| TK Ball FB 3/4 in | Class 900 | 31
| TK Ball FB 3/4 in | Class 1500 | 30
| TK Ball FB 3/4 in | Class 2500 | 29
| TK Ball FB 1 in | Class 150 | 90
| TK Ball FB 1 in | Class 300 | 78
| TK Ball FB 1 in | Class 600 | 69
| TK Ball FB 1 in | Class 900 | 63
| TK Ball FB 1 in | Class 1500 | 63
| TK Ball FB 1 in | Class 2500 | 27
| TK Ball FB 1-1/2 in | Class 150 | 227
| TK Ball FB 1-1/2 in | Class 300 | 211
| TK Ball FB 1-1/2 in | Class 600 | 187
| TK Ball FB 1-1/2 in | Class 900 | 167
| TK Ball FB 1-1/2 in | Class 1500 | 167
| TK Ball FB 1-1/2 in | Class 2500 | 92
| TK Ball FB 2 in | Class 150 | 463
| TK Ball FB 2 in | Class 300 | 420
| TK Ball FB 2 in | Class 600 | 361
| TK Ball FB 2 in | Class 900 | 322
| TK Ball FB 2 in | Class 1500 | 322
| TK Ball FB 2 in | Class 2500 | 291
| TK Ball FB 3 in | Class 150 | 1247
| TK Ball FB 3 in | Class 300 | 1057
| TK Ball FB 3 in | Class 600 | 943
| TK Ball FB 3 in | Class 900 | 911
| TK Ball FB 3 in | Class 1500 | 820
| TK Ball FB 3 in | Class 2500 | 739
| TK Ball FB 4 in | Class 150 | 2489
| TK Ball FB 4 in | Class 300 | 2156
| TK Ball FB 4 in | Class 600 | 1811
| TK Ball FB 4 in | Class 900 | 1760
| TK Ball FB 4 in | Class 1500 | 1610
| TK Ball FB 4 in | Class 2500 | 1450
| TK Ball FB 6 in | Class 150 | 5458
| TK Ball FB 6 in | Class 300 | 5393
| TK Ball FB 6 in | Class 600 | 4581
| TK Ball FB 6 in | Class 900 | 4386
| TK Ball FB 6 in | Class 1500 | 4079
| TK Ball FB 6 in | Class 2500 | 2528
| TK Ball FB 8 in | Class 150 | 10721
| TK Ball FB 8 in | Class 300 | 10235
| TK Ball FB 8 in | Class 600 | 8920
| TK Ball FB 8 in | Class 900 | 8446
| TK Ball FB 8 in | Class 1500 | 7978
| TK Ball FB 8 in | Class 2500 | 5301
| TK Ball FB 10 in | Class 150 | 17756
| TK Ball FB 10 in | Class 300 | 17202
| TK Ball FB 10 in | Class 600 | 14614
| TK Ball FB 10 in | Class 900 | 14164
| TK Ball FB 10 in | Class 1500 | 13029
| TK Ball FB 10 in | Class 2500 | 8431
| TK Ball FB 12 in | Class 150 | 26714
| TK Ball FB 12 in | Class 300 | 25917
| TK Ball FB 12 in | Class 600 | 22782
| TK Ball FB 12 in | Class 900 | 21230
| TK Ball FB 12 in | Class 1500 | 19619
| TK Ball FB 12 in | Class 2500 | 12348
| TK Ball FB 14 in | Class 150 | 32609
| TK Ball FB 14 in | Class 300 | 30936
| TK Ball FB 14 in | Class 600 | 28641
| TK Ball FB 14 in | Class 900 | 26625
| TK Ball FB 14 in | Class 1500 | 24083
| TK Ball FB 16 in | Class 150 | 44627
| TK Ball FB 16 in | Class 300 | 42550
| TK Ball FB 16 in | Class 600 | 39141
| TK Ball FB 16 in | Class 900 | 36642
| TK Ball FB 16 in | Class 1500 | 33110
| TK Ball FB 18 in | Class 150 | 57799
| TK Ball FB 18 in | Class 300 | 56171
| TK Ball FB 18 in | Class 600 | 51396
| TK Ball FB 18 in | Class 900 | 48645
| TK Ball FB 18 in | Class 1500 | 43329
| TK Ball FB 20 in | Class 150 | 74763
| TK Ball FB 20 in | Class 300 | 71830
| TK Ball FB 20 in | Class 600 | 65432
| TK Ball FB 20 in | Class 900 | 62207
| TK Ball FB 20 in | Class 1500 | 55426
| TK Ball FB 22 in | Class 150 | 91770
| TK Ball FB 22 in | Class 300 | 88511
| TK Ball FB 22 in | Class 600 | 81273
| TK Ball FB 24 in | Class 150 | 113221
| TK Ball FB 24 in | Class 300 | 109382
| TK Ball FB 24 in | Class 600 | 98940
| TK Ball FB 24 in | Class 900 | 93948
| TK Ball FB 24 in | Class 1500 | 83892
| TK Ball FB 26 in | Class 150 | 132159
| TK Ball FB 26 in | Class 300 | 126650
| TK Ball FB 26 in | Class 600 | 117426
| TK Ball FB 28 in | Class 150 | 154783
| TK Ball FB 28 in | Class 300 | 148828
| TK Ball FB 28 in | Class 600 | 138726
| TK Ball FB 30 in | Class 150 | 182779
| TK Ball FB 30 in | Class 300 | 176007
| TK Ball FB 30 in | Class 600 | 161903
| TK Ball FB 36 in | Class 150 | 251986
| TK Ball FB 36 in | Class 300 | 248911
| TK Ball FB 36 in | Class 600 | 226668
Reduced Bore
| TK Ball RB 2x1-1/2 in | Class 150 | 125
| TK Ball RB 2x1-1/2 in | Class 300 | 125
| TK Ball RB 2x1-1/2 in | Class 600 | 125
| TK Ball RB 2x1-1/2 in | Class 900 | 124
| TK Ball RB 2x1-1/2 in | Class 1500 | 124
| TK Ball RB 2x1-1/2 in | Class 2500 | -
| TK Ball RB 3x2 in | Class 150 | 183
| TK Ball RB 3x2 in | Class 300 | 183
| TK Ball RB 3x2 in | Class 600 | 183
| TK Ball RB 3x2 in | Class 900 | 183
| TK Ball RB 3x2 in | Class 1500 | 182
| TK Ball RB 3x2 in | Class 2500 | 182
| TK Ball RB 4x3 in | Class 150 | 505
| TK Ball RB 4x3 in | Class 300 | 504
| TK Ball RB 4x3 in | Class 600 | 502
| TK Ball RB 4x3 in | Class 900 | 502
| TK Ball RB 4x3 in | Class 1500 | 501
| TK Ball RB 4x3 in | Class 2500 | 500
| TK Ball RB 6x4 in | Class 150 | 735
| TK Ball RB 6x4 in | Class 300 | 734
| TK Ball RB 6x4 in | Class 600 | 734
| TK Ball RB 6x4 in | Class 900 | 733
| TK Ball RB 6x4 in | Class 1500 | 733
| TK Ball RB 6x4 in | Class 2500 | 732
| TK Ball RB 8x6 in | Class 150 | 2022
| TK Ball RB 8x6 in | Class 300 | 2021
| TK Ball RB 8x6 in | Class 600 | 2018
| TK Ball RB 8x6 in | Class 900 | 2016
| TK Ball RB 8x6 in | Class 1500 | 2014
| TK Ball RB 8x6 in | Class 2500 | 1485
| TK Ball RB 10x6 in | Class 150 | 1458
| TK Ball RB 10x6 in | Class 300 | 1458
| TK Ball RB 10x6 in | Class 600 | 1457
| TK Ball RB 10x6 in | Class 900 | 1457
| TK Ball RB 10x6 in | Class 1500 | 1457
| TK Ball RB 10x6 in | Class 2500 | 1099
| TK Ball RB 10x8 in | Class 150 | 4183
| TK Ball RB 10x8 in | Class 300 | 4181
| TK Ball RB 10x8 in | Class 600 | 4169
| TK Ball RB 10x8 in | Class 900 | 4166
| TK Ball RB 10x8 in | Class 1500 | 4158
| TK Ball RB 10x8 in | Class 2500 | 3307
| TK Ball RB 12x8 in | Class 150 | 2941
| TK Ball RB 12x8 in | Class 300 | 2940
| TK Ball RB 12x8 in | Class 600 | 2939
| TK Ball RB 12x8 in | Class 900 | 2938
| TK Ball RB 12x8 in | Class 1500 | 2937
| TK Ball RB 12x8 in | Class 2500 | 2385
| TK Ball RB 12x10 in | Class 150 | 7342
| TK Ball RB 12x10 in | Class 300 | 7338
| TK Ball RB 12x10 in | Class 600 | 7316
| TK Ball RB 12x10 in | Class 900 | 7302
| TK Ball RB 12x10 in | Class 1500 | 7283
| TK Ball RB 12x10 in | Class 2500 | 5933
| TK Ball RB 14x12 in | Class 150 | 14080
| TK Ball RB 14x12 in | Class 300 | 14043
| TK Ball RB 14x12 in | Class 600 | 13984
| TK Ball RB 14x12 in | Class 900 | 13924
| TK Ball RB 14x12 in | Class 1500 | 13814
| TK Ball RB 16x12 in | Class 150 | 9031
| TK Ball RB 16x12 in | Class 300 | 9027
| TK Ball RB 16x12 in | Class 600 | 9017
| TK Ball RB 16x12 in | Class 900 | 9009
| TK Ball RB 16x12 in | Class 1500 | 8994
| TK Ball RB 16x14 in | Class 150 | 14785
| TK Ball RB 16x14 in | Class 300 | 14765
| TK Ball RB 16x14 in | Class 600 | 14725
| TK Ball RB 16x14 in | Class 900 | 14668
| TK Ball RB 16x14 in | Class 1500 | 14622
| TK Ball RB 18x16 in | Class 150 | 20841
| TK Ball RB 18x16 in | Class 300 | 20821
| TK Ball RB 18x16 in | Class 600 | 20752
| TK Ball RB 18x16 in | Class 900 | 20703
| TK Ball RB 18x16 in | Class 1500 | 20582
| TK Ball RB 20x16 in | Class 150 | 14843
| TK Ball RB 20x16 in | Class 300 | 14837
| TK Ball RB 20x16 in | Class 600 | 14820
| TK Ball RB 20x16 in | Class 900 | 14810
| TK Ball RB 20x16 in | Class 1500 | 14783
| TK Ball RB 20x18 in | Class 150 | 28064
| TK Ball RB 20x18 in | Class 300 | 28023
| TK Ball RB 20x18 in | Class 600 | 27914
| TK Ball RB 20x18 in | Class 900 | 27847
| TK Ball RB 20x18 in | Class 1500 | 27667
| TK Ball RB 24x20 in | Class 150 | 26734
| TK Ball RB 24x20 in | Class 300 | 26720
| TK Ball RB 24x20 in | Class 600 | 26676
| TK Ball RB 24x20 in | Class 900 | 26650
| TK Ball RB 24x20 in | Class 1500 | 26582
| TK Ball RB 30x24 in | Class 150 | 35617
| TK Ball RB 30x24 in | Class 300 | 35604
| TK Ball RB 30x24 in | Class 600 | 35571
| TK Ball RB 30x26 in | Class 150 | 51377
| TK Ball RB 30x26 in | Class 300 | 51337
| TK Ball RB 30x26 in | Class 600 | 51238
| TK Ball RB 36x30 in | Class 150 | 63625
| TK Ball RB 36x30 in | Class 300 | 63565
| TK Ball RB 36x30 in | Class 600 | 63458

## PIPE WT TABLE
ENGINEERING DESIGN DATA - DENNIS KIRK
B 36.10 PIPING NOMINAL SIZE AND WALL THICKNESS LOOKUP TABLE
SIZE | NOM | OD | SCHED | LOC'N | WT | ID
30 | 750 | 762 | STD | 4 | 9.53 | 742.94
#N/A
PIPE WT's - PSA DATA SHEETS 1991
SIZE | NOM | OD | STD | XS | XXS | 5S | 10S | 40S | 10 | 20 | 30 | 40 | 60 | 80 | 100 | 120 | 140 | 160
0.125 | 6 | 10.3 | 1.73 | 2.41 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.73 | #N/A | 2.41 | #N/A | #N/A | #N/A | #N/A
0.25 | 8 | 13.7 | 2.24 | 3.02 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.24 | #N/A | 3.02 | #N/A | #N/A | #N/A | #N/A
0.375 | 10 | 17.1 | 2.31 | 3.2 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.31 | #N/A | 3.2 | #N/A | #N/A | #N/A | #N/A
0.5 | 15 | 21.3 | 2.77 | 3.73 | 7.47 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.77 | #N/A | 3.73 | #N/A | #N/A | #N/A | 4.78
0.75 | 20 | 26.7 | 2.87 | 3.91 | 7.82 | 1.65 | 2.11 | 2.87 | #N/A | #N/A | #N/A | 2.87 | #N/A | 3.91 | #N/A | #N/A | #N/A | 5.56
1 | 25 | 33.4 | 3.38 | 4.55 | 9.09 | 1.65 | 2.77 | 3.38 | #N/A | #N/A | #N/A | 3.38 | #N/A | 4.55 | #N/A | #N/A | #N/A | 6.35
1.5 | 40 | 48.3 | 3.68 | 5.08 | 10.15 | 1.65 | 2.77 | 3.68 | #N/A | #N/A | #N/A | 3.68 | #N/A | 5.08 | #N/A | #N/A | #N/A | 7.14
2 | 50 | 60.3 | 3.91 | 5.54 | 11.07 | 1.65 | 2.77 | 3.91 | #N/A | #N/A | #N/A | 3.91 | #N/A | 5.54 | #N/A | #N/A | #N/A | 8.74
3 | 80 | 88.9 | 5.49 | 7.62 | 15.24 | 2.11 | 3.05 | 5.49 | #N/A | #N/A | #N/A | 5.49 | #N/A | 7.62 | #N/A | #N/A | #N/A | 11.13
4 | 100 | 114.3 | 6.02 | 8.56 | 17.12 | 2.11 | 3.05 | 6.02 | #N/A | #N/A | #N/A | 6.02 | #N/A | 8.56 | #N/A | 11.13 | #N/A | 13.49
6 | 150 | 168.3 | 7.11 | 10.97 | 21.95 | 2.77 | 3.4 | 7.11 | #N/A | #N/A | #N/A | 7.11 | #N/A | 10.97 | #N/A | 14.27 | #N/A | 18.26
8 | 200 | 219.1 | 8.18 | 12.7 | 22.23 | 2.77 | 3.76 | 8.18 | #N/A | 6.35 | 7.04 | 8.18 | 10.31 | 12.7 | 15.09 | 18.26 | 20.62 | 23.01
10 | 250 | 273.1 | 9.27 | 12.7 | 25.4 | 3.4 | 4.19 | 9.27 | #N/A | 6.35 | 7.8 | 9.27 | 12.7 | 15.09 | 18.26 | 21.44 | 25.4 | 28.58
12 | 300 | 323.9 | 9.53 | 12.7 | 25.4 | 3.96 | 4.57 | 9.52 | #N/A | 6.35 | 8.38 | 10.31 | 14.27 | 17.48 | 21.44 | 25.4 | 28.58 | 33.32
14 | 350 | 355.6 | 9.53 | 12.7 | #N/A | 3.96 | 4.78 | #N/A | 6.35 | 7.92 | 9.53 | 11.13 | 15.09 | 19.05 | 23.83 | 27.79 | 31.75 | 35.71
16 | 400 | 406.4 | 9.53 | 12.7 | #N/A | 4.19 | 4.78 | #N/A | 6.35 | 7.92 | 9.53 | 12.7 | 16.66 | 21.44 | 26.19 | 30.96 | 36.53 | 40.49
18 | 450 | 457 | 9.53 | 12.7 | #N/A | 4.19 | 4.78 | #N/A | 6.35 | 7.92 | 11.13 | 14.27 | 19.05 | 23.83 | 29.36 | 34.93 | 39.67 | 45.24
20 | 500 | 508 | 9.53 | 12.7 | #N/A | 4.78 | 5.54 | #N/A | 6.35 | 9.53 | 12.7 | 15.09 | 20.62 | 26.19 | 32.54 | 38.1 | 44.45 | 50.01
22 | 550 | 559 | 9.53 | 12.7 | #N/A | #N/A | #N/A | #N/A | 6.35 | 9.53 | 12.7 | #N/A | 22.23 | 28.58 | 34.93 | 41.28 | 47.63 | 53.98
24 | 600 | 610 | 9.53 | 12.7 | #N/A | 5.54 | 6.35 | #N/A | 6.35 | 9.53 | 14.27 | 17.48 | 24.61 | 30.96 | 38.89 | 46.02 | 52.37 | 59.54
26 | 650 | 660 | 9.53 | 12.7 | #N/A | #N/A | #N/A | #N/A | 7.92 | 12.7 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
28 | 700 | 711 | 9.53 | 12.7 | #N/A | #N/A | #N/A | #N/A | 7.92 | 12.7 | 15.88 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
30 | 750 | 762 | 9.53 | 12.7 | #N/A | 6.35 | 7.92 | #N/A | 7.92 | 12.7 | 15.88 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
32 | 800 | 813 | 9.53 | 12.7 | #N/A | #N/A | #N/A | #N/A | 7.92 | 12.7 | 15.88 | 17.48 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
34 | 850 | 864 | 9.53 | 12.7 | #N/A | #N/A | #N/A | #N/A | 7.92 | 12.7 | 15.88 | 17.48 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
36 | 900 | 914 | 9.53 | 12.7 | #N/A | #N/A | #N/A | #N/A | 7.92 | 12.7 | 15.88 | 19.05 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
42 | 1050 | 1067 | 9.53 | 12.7 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
LOCATION OF ID INFO FOR EACH PIPE SIZE
2 | 2 | 1 | 3 | 4
80 | 80 | 160 | 40 | 40
15 | 15 | 19 | 13 | 13 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
15 | 15 | 19 | 13 | 13 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AMERON GRE PIPING: |  |  | Surface Roughness 5.3 x 10-6 m (0.0053 mm)
| NOMINAL SIZE |  | INCHES | 1 | 1.5 | 2 | 3 | 4 | 6 | 8 | 10 | 12 | 14 | 16 | 18 | 20 | 24 | 30 | 36
BONDSTRAND 2000 |  |  | ID MM | 27 | 42 | 53 | 82 | 105 | 159 | 209 | 263 | 314 | 344 | 394
| 1100 - 3100 kPa |  | WT MM | 3.6 | 3.6 | 4 | 4 | 5.2 | 5.2 | 5.7 | 5.7 | 5.7 | 6.4 | 6.8
BONDSTRAND 2000M |  |  | ID MM | 25 | 38 | 53.1 | 81.8 | 105.2 | 159 | 208.8 | 262.9 | 313.7 | 337.6 | 385.8 | 433.8 | 482.1 | 578.6 | 723.1 | 867.9
| 1000 - 1500 kPa |  | WT MM | 4.3 | 5.5 | 4.1 | 4.1 | 5.2 | 5.4 | 7 | 8.6 | 10.2 | 11 | 12.5 | 13.9 | 15.4 | 18.3 | 22.6 | 27.3
Typical Values for surface roughness e (mm)
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
| Glass | Drawn Tube | Copper | GRP Pipe | Stainless Steel | Steel Pipe-clean | Steel Pipe-new | Steel 6 mo | Steel 12 mo | Steel 24 mo | Steel Pigged | Stl Sand Blast | Epoxy Lined | Galvanised Iron | Cast Iron | Concrete-smooth | Concrete-rough | N/A | N/A | N/A
| 0.001 | 0.0015 | 0.0035 | 0.0053 | 0.03 | 0.05 | 0.019 | 0.03 | 0.04 | 0.05 | 0.01 | 0.007 | 0.007 | 0.15 | 0.26 | 0.3 | 3 | N/A | N/A | N/A
feet | 3.2808e-06 | 4.9213e-06 | 1.1483e-05 | 1.7388e-05 | 9.8425e-05 | 0.00016404 | 6.2336e-05 | 9.8425e-05 | 0.00013123 | 0.00016404 | 3.2808e-05 | 2.2966e-05 | 2.2966e-05 | 0.00049213 | 0.00085302 | 0.00098425 | 0.0098425 | #VALUE! | #VALUE! | #VALUE!